## Slide 1
Hisense HiMod chiller

## Slide 2
Műszaki adatok
Page number format
Hi Mod
Model |  |  | HFRWVE-65SPF/AE | HFRWVE-130DPF/AE
Cooling capacity |  | kW | 63 | 126
Heating capacity |  | kW | 68 | 136
COPc/COPh |  |  | 2.85/3.04 | 2.9/3.05
SEER |  |  | 4.71 | 4.61
SCOP（average，Outlet 45℃） |  |  | 2.87 | 2.91
Capacity adjustment of single unit |  |  | Inverter stepless | 
Power supply |  |  | 380V-415V 3N～ 50Hz | 
Compressor |  |  | DD110 (25HP) enhanced vapor injection scroll compressor from Hitachi, Guangzhou | 
Compressor quantity |  | set | 1 | 2
Water side HEX type |  |  | Plate HEX | 
Water side design pressure |  |  | 1.0MPa | 
Rated water flow |  | m3/h | 11.2 | 22.4
Water resistance(without filter) |  | kPa | 35 | 35
Water resistance(with filter) |  | kPa | 45 | 45
Pipe diameter(inlet/outlet) |  | — | G2-1/2 External thread（DN65） | 
Fan | Type | — | Low noise DC variable frequency axial flow fan | 
 | Air flow rate | m3/h | 24400 | 43000
 | QTY | set | 2 | 2
Refrigerant | Type | - | R410A | 
 | Total charge | kg | 15.5 | 2*14
Outline dimension | L | mm | 1950 | 2190
 | W | mm | 765 | 1100
 | H | mm | 1725 | 2360
Weight | Net weight | kg | 490 | 910
 | Operation weight | kg | 510 | 930
Noise dB(A) (sound power level) |  |  | 81 | 84
Noise dB(A) (sound pressure level) |  |  | 68 | 70

## Slide 3
Bemutató
Page number format
Fűtési üzemmód
HFRWVE-130DPF/AE
HFRWVE-65SPF/AE
Chart: Fűtés
| -26 | -26 | -5 | 43 | 43 | -26
制热 | 35.2 | 45 | 55.2 | 55 | 35.2 | 35.2
Minőségi tanusítványok:
EU RoHS 2.0, WEEE
CE
Product series：Hisense Inverter VE1 series
Model | HFRWVE-65SPF/AE | HFRWVE-130DPF/AE
Hűtő teljesítmény | 63kW | 126kW
Fűtő teljesítmény | 68kW | 136kW
Compresszor | Inv | Inv
Hűtési üzemmód
Chart: Hűté
| -15 | -15 | 48 | 48 | -15
制冷 | 5 | 15 | 15 | 5 | 5
Hi Mod

## Slide 4
Szabad kombinációk, intelligens vezérlés
Page number format
16 modul;
Frekvencia szabályzás 20 and 100 %
Standard RS-485 komunikációs adapter
Opcionnális Távvezérlő egység ( APP and web remote control).
Chiller cloud platform
IoT cloud platform (a jövőben)
LTE wireless network, wired hálózat támogatás
Könnyen telepíthető rendszer
Távoli elérés: gateway
(bevezetés alatt)
Fali vezérlő
Hi Mod

## Slide 5
Kombináció
Page number format
Hi Mod
16 Egység : Teljesítmény 65 - 2085 Kw

## Slide 6
Smart defrost ( „okos leolvasztás”) technológia
Page number format
The fin heat exchanger is equipped with dual temperature sensors, which can accurately determine the frosting state, and intelligently judge according to the ambient temperature, evaporation temperature and operating time, and defrost in time;
The defrosting time is automatically adjusted to reduce invalid defrosting, prolong the defrosting time, and improve the heating efficiency;
When the modules are combined, the number of defrost systems at the same time can be set from 1 to 16;
Under standard conditions, the longest defrosting interval defaults to 2 hours, which can be adjusted;
The single module is designed as a double fluorine single water system, the water side heat exchanger is shared, and the air side heat exchanger is separated, and the unit load is controlled by the total inlet and outlet water temperature;
The wind side of the dual system is completely separated and can operate independently. Rotational defrosting of the finned heat exchanger of the entire unit is realized.
Hi Mod

## Slide 7
High Efficiency Finned Condenser
Page number format
3 Main Components
7mm high-efficiency internal thread heat exchange tube, small size and high heat transfer coefficient;
Window-type aluminum fins, hydrophilic coating, slow down the formation of frost, facilitate the rapid removal of defrosted water, and improve heating performance ;
The anti-frost design at the bottom of the heat exchanger can effectively prevent the accumulation of the lower frost layer.
Fin HEX | Type | — | High Efficiency Internal Threaded Pipe
 | Diameter | mm | 7
 | Rows | — | 3
 | Forms | — | Louvered
 | Material | — | Hydrophilic aluminum foil 0.105mm
 | Pitch | mm | 1.7
frost-free bottom
The lowermost branch is provided with a one-way valve, which can circulate during cooling, but not during heating, reducing frost formation.
Hisense

## Slide 8
Page number format
(1) Betáp
380-415V AC 3N~ 50Hz ;
Megengedett maximális feszültség ingadozás ± 10%
Megengedet 3ph ingadozás alatt 2%.
(3) Kialakítás
Temp. | Range
Cooling ambient temperature | -15～48℃
Heating ambient temperature | -26～43℃
Outlet temperature of cooling | 5～15℃
Outlet temperature of heating | 35～55℃
Chart: Heating
| -26 | -26 | -5 | 43 | 43 | -26
制热 | 35.2 | 45 | 55.2 | 55 | 35.2 | 35.2
Fűtési hőmérsékllet
Hi Mod
(2) Működési hőmérsékletek
Hitach EVI kompresszor
Economizer
Előnyök:
Tkh= -5°C Twout= 55°C
Tkh= -25°C Twout= 45°C

## Slide 9
Economizer
Page number format
3 Main Components
The economizer adopts high-efficiency plate heat exchanger, which is light in weight,
high in heat exchange efficiency and good in reliability;
The economizer adopts the Danfoss brand with first-class quality；
The use of the economizer greatly improves the subcooling degree of the refrigerant
and the energy efficiency ratio of the unit.
Economizer
EVI compressor
Exhaust
Hisense

## Slide 10
Page number format
Tartozékok
Szűrő és víz áramlás őr
Communikációs kábel 30m
Szensor cső, 2 sets
Szenzor rögzítő, 2 sets
Fali vezérlő
RS485 protokol interface
Kommunikációs csatorna
Termisztor
Hi Mod

## Slide 11
Page number format
Víz szűrő
Stainless Steel Water Filter
Cserélhető betét
Bemenő
Kimenő
Bekötések
Hi Mod

## Slide 12
Page number format
Elektromos modul
Elektromos egység bekötése
Hi Mod

## Slide 13
Servíz támogatás
Intelligens szerviz felügyelet: DATA COLLECTOR, Hi Checker
- Üzem információk lekérdezése, beállítások
- Rendszer felügyelet ellenőrzése
- Távoli diagnosztika felmérés és javítás, monitoring
- „Hi Service” mobil applikáció: letölthető a Mobil Apps store-ból ingyen

## Slide 14
Műszaki és tervezői háttértámogatás
Selection Software
Design software (AutoCAD)
HVAC műszaki támogatás
Web oldalak
www.hisense-vrf.hu
www.hisensehvac.com